SBC 401-CR-2024

Vision-Detectable Rules

Vector Database Reference Document

Saudi Electrical Code — Structured Rule Extract for Vector DB Embedding

Total Rules: 192  |  Categories: 22  |  Excluded (Physical Testing): 12

Generated: 2026-05-18

Table of Contents

1. Document Overview	2

2. Rule Classification Methodology	3

3. Equipment Presence & Placement Rules	4

4. Labeling, Identification & Signage Rules	10

5. Wiring System Visual Rules	14

6. Protective Device Visibility Rules	20

7. Special Location Zone Compliance Rules	25

8. Earthing & Bonding Visual Rules	30

9. Emergency & Safety Service Rules	34

10. IP Rating & Environmental Marking Rules	38

11. Verification Inspection Visual Rules	41

12. Physical Protection Rules	46

13. Thermal Protection Rules	50

14. EMI & Special Installation Rules	55

EM — EMI Protection Rules	55

PV — Photovoltaic Installation Rules	57

SN — Sauna Location Rules	62

CS — Construction Site Rules	64

AG — Agricultural Premises Rules	65

CR — Confined/Restricted Location Rules	68

CV — Caravan/Camping Park Rules	69

MR — Marina Rules	71

EX — Exhibition/Show Rules	73

OL — Outdoor Lighting Rules	76

EL — Extra-low Voltage Lighting Rules	77

MO — Mobile/Transportable Unit Rules	80

15. Excluded Rules — Physical Testing Required	82

Note: Right-click the Table of Contents and select “Update Field” to refresh page numbers after opening.

# 1. Document Overview

This document provides a structured technical reference for all rules extracted from the Saudi Building Code — Electrical Installations SBC 401-CR-2024 that are detectable by visual inspection alone, without requiring electrical measurement, instrumented testing, or engineering calculations. The extracted rules are formatted as self-contained data blocks, each containing the SBC 401 clause reference, the full regulatory text, a detection type classification, a visual detection target, a category assignment, and a priority level.

The primary purpose of this document is to serve as the source content for vector database ingestion. Each rule block is designed as an independent, self-contained unit that can be chunked, embedded, and retrieved without cross-rule narrative dependencies. The consistent formatting enables reliable automated parsing, and the SBC reference code in each block ensures full traceability to the source standard.

A total of 192 vision-detectable rules have been extracted from SBC 401-CR-2024 across 22 categories, covering chapters 41 through 61 and special location sections 701 through 717. An additional 12 rule categories requiring physical testing instruments have been identified and excluded; these are documented in Section 15 for reference.

# 2. Rule Classification Methodology

Rules were classified as vision-detectable if their compliance or non-compliance can be determined from visual observation alone — using photographs, video frames, or direct visual inspection — without requiring electrical measurement, instrumented testing, or engineering calculations. This classification criterion ensures that every rule in this document can, in principle, be verified by a visual inspection system or a human inspector using only their eyes and without test instruments.

Seven detection types are used to classify how each rule can be visually verified:

PRESENCE: The rule requires a specific equipment, device, sign, or component to exist at a location. Compliance is confirmed by detecting the object; non-compliance is indicated by its absence. Examples: RCD device in distribution board, fire barrier at cable penetration, earthing conductor from electrode to MET.

ABSENCE: The rule prohibits a specific equipment, device, or component from a location. Compliance is confirmed by the absence of the prohibited object; non-compliance is indicated by its presence. Examples: no socket-outlets in bathroom Zone 0, no standard household AC plugs in PV arrays, no PEN conductor connections in fire-risk locations.

COLOR: The rule specifies a required color for identification of a conductor, cable, or component. Compliance is confirmed by detecting the correct color; non-compliance by an incorrect or missing color. Examples: green-yellow PE conductor insulation, blue neutral conductor, pink functional earthing conductor in PV installations.

POSITION: The rule specifies a mounting height, zone boundary, or spatial location where equipment must or must not be installed. Compliance is confirmed by verifying the equipment position against zone definitions or height requirements. Examples: equipment in correct bathroom zone, socket-outlets at 0.5–1.5m height in caravan parks, switchgear outside sauna rooms.

LABEL: The rule requires visible text, markings, signage, or identification on equipment or at locations. Compliance is confirmed by detecting and reading the label content; non-compliance by a missing or illegible label. Examples: “ELECTRICAL ROOM” sign on door, circuit identification labels on distribution boards, IP code marking on enclosures, “SOLAR DC” marking on PV equipment.

SPACING: The rule specifies a minimum clearance, separation distance, or working space between equipment and other objects. Compliance is confirmed by measuring the distance between detected objects; non-compliance by insufficient clearance. Examples: luminaire distance from combustible materials, power/ICT cable separation, working space around electrical panels.

CONDITION: The rule requires equipment to be in a specific physical state — such as closed, intact, undamaged, non-combustible, or properly enclosed. Compliance is confirmed by classifying the physical state of the detected object; non-compliance by an incorrect or degraded state. Examples: enclosure cover closed and undamaged, non-combustible material around heat-producing equipment, IP-rated enclosure in wet locations.

Rules requiring the following types of verification were excluded: insulation resistance testing (megger), earth continuity/resistance testing, RCD trip time testing, voltage drop calculations, current carrying capacity calculations, short circuit current calculations, earth fault loop impedance testing, polarity testing, and any measurement requiring test instruments. These 12 excluded categories are documented in Section 15.

# 3. Equipment Presence & Placement Rules

The following 14 rules are extracted from Ch. 51, 53, 55 of SBC 401-CR-2024. Each rule block contains the SBC reference code, the full rule text, the detection type, the visual detection target, and the priority level.

[EP-001]  SBC Ref: 51-3.1    Detection: PRESENCE    Priority: HIGH

Rule Text: All equipment, including wiring, shall be arranged to facilitate its operation, inspection and maintenance and access to its connections.

Visual Target: Equipment accessibility; clear working space around panels

[EP-002]  SBC Ref: 51-3.1    Detection: SPACING    Priority: HIGH

Rule Text: Equipment likely to require examination, adjustment, servicing, or maintenance while energized shall have clear working space in the direction of access to live parts, not less than specified in Chapter 729.

Visual Target: Clear working space dimensions around electrical equipment

[EP-003]  SBC Ref: 51-4.1    Detection: LABEL    Priority: HIGH

Rule Text: Doors into electrical control panel rooms shall be marked with a plainly visible and legible sign stating 'electrical room' or similar approved wording.

Visual Target: Sign 'ELECTRICAL ROOM' on door

[EP-004]  SBC Ref: 51-4.1    Detection: LABEL    Priority: MEDIUM

Rule Text: Labels or other suitable means of identification shall be provided to indicate the purpose of switchgear and controlgear, unless there is no possibility of confusion.

Visual Target: Identification labels on switchgear and controlgear

[EP-005]  SBC Ref: 51-4.1    Detection: PRESENCE    Priority: HIGH

Rule Text: Where the functioning of switchgear and controlgear cannot be observed by the operator, and where this might cause a danger, a suitable indicator complying with IEC 60073 and IEC 60447 shall be fixed in a position visible to the operator.

Visual Target: Status indicator lights on switchgear

[EP-006]  SBC Ref: 53-6.2.1.1    Detection: PRESENCE    Priority: HIGH

Rule Text: Every circuit shall be capable of being isolated from all live conductors. Each supply shall have a means of isolation.

Visual Target: Isolation device present per circuit

[EP-007]  SBC Ref: 53-6.2.1.2    Detection: PRESENCE    Priority: HIGH

Rule Text: Suitable means shall be provided to prevent any equipment from being inadvertently or unintentionally energized.

Visual Target: Lock-off or warning tag on isolation devices

[EP-008]  SBC Ref: 53-6.4    Detection: PRESENCE    Priority: HIGH

Rule Text: Emergency switching shall be provided where electrically powered equipment constitutes a hazard that needs to be rapidly disconnected from supply.

Visual Target: Emergency stop button/switch at identified hazard locations

[EP-009]  SBC Ref: 55-6.1    Detection: PRESENCE    Priority: MEDIUM

Rule Text: Socket-outlets shall be provided in accordance with the installation requirements for the intended use of the building.

Visual Target: Socket-outlets present per room function

[EP-010]  SBC Ref: 55-8.9    Detection: LABEL    Priority: MEDIUM

Rule Text: Electric appliances shall be marked with the rated voltage, rated current or power input, and the manufacturer name or trademark.

Visual Target: Nameplate/marking on electric appliances

[EP-011]  SBC Ref: 55-9.5.4    Detection: PRESENCE    Priority: MEDIUM

Rule Text: If the luminaire does not provide connecting devices for connection to the supply, the connecting devices shall be terminals per IEC 60998 or DCL plug per IEC 61995 or installation couplers per IEC 61535.

Visual Target: Proper luminaire connection device visible

[EP-012]  SBC Ref: 55-9.6    Detection: LABEL    Priority: MEDIUM

Rule Text: Only independent lamp controlgear marked as suitable for independent use shall be used external to a luminaire (IEC 60417-5138 symbol).

Visual Target: Independent-use marking symbol on controlgear

[EP-013]  SBC Ref: 55-9.10.1    Detection: CONDITION    Priority: HIGH

Rule Text: Luminaires installed in wet locations shall be installed so that water cannot enter or accumulate in wiring compartments, lampholders, or other electrical parts.

Visual Target: Proper luminaire enclosure condition in wet areas

[EP-014]  SBC Ref: 55-9.11    Detection: LABEL    Priority: HIGH

Rule Text: In zones 0 and 1 hazardous locations, each luminaire shall be identified as a complete assembly for the zone and clearly marked to indicate the maximum wattage of lamps.

Visual Target: Zone-rated label and max wattage marking on luminaires

# 4. Labeling, Identification & Signage Rules

The following 12 rules are extracted from Ch. 51, 55, 712, 722, D.57 of SBC 401-CR-2024. Each rule block contains the SBC reference code, the full rule text, the detection type, the visual detection target, and the priority level.

[LI-001]  SBC Ref: 51-4.2.1    Detection: LABEL    Priority: MEDIUM

Rule Text: Wiring shall be so arranged or marked that it can be identified for inspection, testing, repairs or alteration of the installation.

Visual Target: Wire identification markers/labels at terminals

[LI-002]  SBC Ref: 51-4.2.2    Detection: COLOR    Priority: MEDIUM

Rule Text: Where an electrical conduit is required, it shall be distinguished from a pipeline or other services.

Visual Target: Conduit visually distinct from other services

[LI-003]  SBC Ref: 51-4.2.3    Detection: COLOR    Priority: HIGH

Rule Text: Identification of conductors by color for electrical installations shall be according to Table 51-2.

Visual Target: Conductor insulation colors per Table 51-2

[LI-004]  SBC Ref: 51-4.2.4    Detection: LABEL    Priority: HIGH

Rule Text: Where an alteration or addition is made to an installation wired in old colors with an extension in new colors, alphanumeric marking for both old and new conductors at the interface shall be according to Table 51-2.

Visual Target: Alphanumeric conductor markings at old/new color interface

[LI-005]  SBC Ref: 51-4.2.5    Detection: LABEL    Priority: HIGH

Rule Text: Where an alteration or addition has been made, a warning sign in Arabic and English shall be fixed at the interface between old and new installations on or near the consumer distribution board.

Visual Target: Bilingual warning sign at distribution board for mixed color installations

[LI-006]  SBC Ref: 51-4.3    Detection: LABEL    Priority: HIGH

Rule Text: The protective devices shall be arranged and identified so that the circuits protected may be easily recognized; for this purpose it may be convenient to group them in distribution boards.

Visual Target: Circuit identification labels on protective devices in distribution boards

[LI-007]  SBC Ref: 51-4.4.1    Detection: PRESENCE    Priority: MEDIUM

Rule Text: Where appropriate, diagrams, charts or tables per IEC 81346-1 and IEC 61082 shall be provided indicating the type and composition of circuits and the identification of devices performing protection, isolation and switching functions and their locations.

Visual Target: Circuit diagrams/charts posted at distribution boards

[LI-008]  SBC Ref: 51-4.4.2    Detection: LABEL    Priority: LOW

Rule Text: The symbols used in diagrams shall be chosen from IEC 60617.

Visual Target: IEC 60617 standard symbols on diagrams

[LI-009]  SBC Ref: 55-8.9    Detection: LABEL    Priority: MEDIUM

Rule Text: Electric appliances shall be marked with the rated voltage, rated current or power input, and the manufacturer name or trademark.

Visual Target: Appliance nameplate with voltage, current/power, manufacturer

[LI-010]  SBC Ref: 712:51-4    Detection: LABEL    Priority: HIGH

Rule Text: PV installation: DC circuits shall be identified at all points of access and at each end of every conductor.

Visual Target: PV DC circuit identification labels

[LI-011]  SBC Ref: 722:55-101    Detection: LABEL    Priority: HIGH

Rule Text: Socket-outlets and vehicle connectors for EV charging shall be of a type identified for the purpose and clearly marked.

Visual Target: EV charging socket-outlet type marking

[LI-012]  SBC Ref: D.57    Detection: LABEL    Priority: HIGH

Rule Text: Battery rooms and enclosures shall have identification labels and warning notices indicating voltage, hazard, and access restrictions.

Visual Target: Warning notice on battery room/enclosure

# 5. Wiring System Visual Rules

The following 14 rules are extracted from Ch. 52, 44 of SBC 401-CR-2024. Each rule block contains the SBC reference code, the full rule text, the detection type, the visual detection target, and the priority level.

[WS-001]  SBC Ref: 52-2.1    Detection: CONDITION    Priority: HIGH

Rule Text: Wiring systems shall be selected and erected so that they can withstand the ambient temperature (AA) expected at the installation location. Equipment shall be selected per Table 51-1 external influences.

Visual Target: Wiring type appropriate for ambient conditions; no heat-damaged insulation

[WS-002]  SBC Ref: 52-2.2    Detection: SPACING    Priority: HIGH

Rule Text: Wiring systems shall be placed sufficiently far from heat sources or shall be protected against the effects of heat, including radiant heat, by shields or other suitable means.

Visual Target: Shield/spacing between wiring and heat sources

[WS-003]  SBC Ref: 52-2.3    Detection: CONDITION    Priority: HIGH

Rule Text: Wiring systems in locations with presence of water (AD) or high humidity (AB) shall be selected and erected to prevent water ingress or accumulation. IP rating marking shall be visible.

Visual Target: IP-rated enclosures and conduit in wet/humid areas

[WS-004]  SBC Ref: 52-2.4    Detection: CONDITION    Priority: MEDIUM

Rule Text: Wiring systems in locations with presence of solid foreign bodies (AE) shall have appropriate degree of protection (IP code) marked on enclosures.

Visual Target: IP-rated enclosures where dust/solid foreign bodies present

[WS-005]  SBC Ref: 52-2.6    Detection: CONDITION    Priority: MEDIUM

Rule Text: Wiring systems subject to impact (AG) shall be protected by location or by additional mechanical protection such as conduit, trunking, or armor.

Visual Target: Mechanical protection on wiring in impact-prone areas

[WS-006]  SBC Ref: 52-7.1    Detection: PRESENCE    Priority: HIGH

Rule Text: Precautions within a fire-segregated compartment: wiring systems shall not reduce the fire integrity of the compartment. Fire barriers shall be maintained at penetration points.

Visual Target: Fire barrier/seal at wiring penetrations through compartment walls

[WS-007]  SBC Ref: 52-7.2    Detection: PRESENCE    Priority: HIGH

Rule Text: Sealing of wiring system penetrations: where wiring systems pass through fire-rated walls or floors, the openings shall be sealed to maintain the fire resistance rating.

Visual Target: Fire-rated seal at cable entry through walls/floors

[WS-008]  SBC Ref: 52-8.1    Detection: SPACING    Priority: MEDIUM

Rule Text: Proximity to electrical services: wiring systems for different voltage levels or different types of circuits shall be adequately separated or segregated.

Visual Target: Separation between power and communication cables

[WS-009]  SBC Ref: 52-8.3    Detection: SPACING    Priority: MEDIUM

Rule Text: Proximity to non-electrical services: electrical wiring shall not be run in the same conduit, trunking or duct as non-electrical services unless effectively separated.

Visual Target: No mixed electrical/non-electrical services in same conduit

[WS-010]  SBC Ref: 44-4.7    Detection: SPACING    Priority: MEDIUM

Rule Text: Cable management systems for power and information technology cables shall be arranged to minimize electromagnetic interference. Physical separation or use of separate cable trays is required.

Visual Target: Separate cable trays/management for power vs IT cables

[WS-011]  SBC Ref: 44-R19    Detection: POSITION    Priority: MEDIUM

Rule Text: Cables in metal cable-trays: preferred arrangement places power cables and signal cables on separate trays or with physical separation within the same tray.

Visual Target: Cable arrangement pattern on metal cable trays

[WS-012]  SBC Ref: 44-R20    Detection: CONDITION    Priority: MEDIUM

Rule Text: Continuity of metallic system components: metallic conduit, trunking, and cable tray sections shall be effectively bonded and connected to maintain electrical continuity.

Visual Target: Intact metallic bonding between conduit/trunking sections

[WS-013]  SBC Ref: 52-2.11    Detection: CONDITION    Priority: MEDIUM

Rule Text: Wiring systems exposed to solar radiation (AN) and ultraviolet radiation shall be of a type resistant to such exposure, or shall be provided with suitable protection.

Visual Target: UV-resistant cable sheathing or protective covering on outdoor wiring

[WS-014]  SBC Ref: 52-2.12    Detection: SPACING    Priority: LOW

Rule Text: Wiring systems in seismic areas (AP) shall be installed with suitable supports and fixings to withstand seismic effects. Flexible connections shall be provided where necessary.

Visual Target: Seismic bracing on cable trays and conduit

# 6. Protective Device Visibility Rules

The following 12 rules are extracted from Ch. 53 of SBC 401-CR-2024. Each rule block contains the SBC reference code, the full rule text, the detection type, the visual detection target, and the priority level.

[PD-001]  SBC Ref: 53-1.2    Detection: PRESENCE    Priority: HIGH

Rule Text: Devices for automatic disconnection of supply (circuit breakers, fuses, RCDs) shall be provided for protection against electric shock in TN, TT, and IT systems.

Visual Target: Circuit breakers/fuses/RCDs present at distribution board

[PD-002]  SBC Ref: 53-1.6    Detection: PRESENCE    Priority: HIGH

Rule Text: Devices for additional protection: residual current protective devices (RCDs) with rated residual operating current not exceeding 30 mA shall be provided for socket-outlets intended for use by ordinary persons.

Visual Target: RCD (30 mA) present in circuit for general-purpose socket-outlets

[PD-003]  SBC Ref: 53-1.7    Detection: PRESENCE    Priority: MEDIUM

Rule Text: Monitoring devices shall be provided where required for protective measures, such as insulation monitoring devices in IT systems.

Visual Target: Insulation monitoring device present in IT system installations

[PD-004]  SBC Ref: 53-2.3    Detection: PRESENCE    Priority: MEDIUM

Rule Text: Arc fault detection devices (AFDDs) shall be selected and installed in accordance with the requirements for locations with particular risk of fire, as specified in Section 42-2.

Visual Target: AFDD present in fire-risk location circuits

[PD-005]  SBC Ref: 53-3.1    Detection: LABEL    Priority: HIGH

Rule Text: Devices for protection against overcurrent (OCPDs) shall be clearly identified with their rated current and breaking capacity markings visible.

Visual Target: Rated current and breaking capacity labels on OCPDs

[PD-006]  SBC Ref: 53-4.1    Detection: PRESENCE    Priority: HIGH

Rule Text: Surge protective devices (SPDs) shall be installed where required by Section 44-3 for protection against transient overvoltages of atmospheric origin.

Visual Target: SPD present at origin of installation (where required)

[PD-007]  SBC Ref: 53-4.4.3    Detection: POSITION    Priority: MEDIUM

Rule Text: SPDs shall be installed as close as practicable to the origin of the installation and to the incoming protective conductor connection. Connecting leads shall be as short as practicable.

Visual Target: SPD mounted near main distribution board origin

[PD-008]  SBC Ref: 53-4.4.9    Detection: SPACING    Priority: MEDIUM

Rule Text: Where the distance between the SPD and the equipment to be protected is greater than 10 m, additional protective measures should be provided, such as an additional SPD close to the equipment.

Visual Target: Additional SPD near equipment if distance > 10 m from origin SPD

[PD-009]  SBC Ref: 53-6.2    Detection: LABEL    Priority: HIGH

Rule Text: Isolating devices shall be clearly identified and indicate the isolated position. The off position shall be clearly indicated.

Visual Target: ON/OFF position indicator on isolating devices

[PD-010]  SBC Ref: 53-6.3    Detection: PRESENCE    Priority: MEDIUM

Rule Text: Switching-off for mechanical maintenance: a device shall be provided to enable equipment to be switched off safely for mechanical maintenance, and shall be clearly identified.

Visual Target: Mechanical maintenance switch with identification label

[PD-011]  SBC Ref: 53-6.4    Detection: PRESENCE    Priority: HIGH

Rule Text: Emergency switching: a device shall be provided for emergency disconnection of supply to any equipment that may give rise to danger. It shall be readily identifiable and accessible.

Visual Target: Emergency switch/button (red, clearly marked)

[PD-012]  SBC Ref: G.53-1    Detection: LABEL    Priority: HIGH

Rule Text: RCD type marking: RCDs shall be marked with their type designation (AC, A, F, or B) to indicate their behavior in the presence of DC components.

Visual Target: RCD type label (AC/A/F/B) visible on device

# 7. Special Location Zone Compliance Rules

The following 15 rules are extracted from Sec. 701, 702, 710, 722, 720 of SBC 401-CR-2024. Each rule block contains the SBC reference code, the full rule text, the detection type, the visual detection target, and the priority level.

[SL-001]  SBC Ref: 701:3    Detection: POSITION    Priority: HIGH

Rule Text: Bathrooms: zones 0, 1, and 2 are defined by dimensions from the bathtub or shower. Only equipment permitted in each zone shall be installed. Zone 0 = inside bathtub/shower; Zone 1 = above bathtub up to 2.25 m; Zone 2 = 0.6 m beyond Zone 1.

Visual Target: No prohibited equipment in bathroom zones 0, 1, 2

[SL-002]  SBC Ref: 701:41    Detection: ABSENCE    Priority: HIGH

Rule Text: In bathroom Zone 0, no switchgear, controlgear, or socket-outlets shall be installed.

Visual Target: No switches/sockets in bathroom Zone 0

[SL-003]  SBC Ref: 701:41    Detection: ABSENCE    Priority: HIGH

Rule Text: In bathroom Zone 1, only equipment specifically designed for Zone 1 may be installed. Socket-outlets are prohibited.

Visual Target: No socket-outlets in bathroom Zone 1

[SL-004]  SBC Ref: 701:41-5.2    Detection: PRESENCE    Priority: HIGH

Rule Text: Supplementary equipotential bonding shall be provided in locations containing a bathtub or shower, connecting all exposed-conductive-parts and extraneous-conductive-parts.

Visual Target: Supplementary bonding conductors visible in bathroom

[SL-005]  SBC Ref: 702:3    Detection: POSITION    Priority: HIGH

Rule Text: Swimming pools: zones 0, 1, and 2 defined. Zone 0 = inside pool; Zone 1 = above pool rim up to 2.5 m; Zone 2 = 2 m beyond Zone 1.

Visual Target: No prohibited equipment in pool zones 0, 1, 2

[SL-006]  SBC Ref: 702:53    Detection: ABSENCE    Priority: HIGH

Rule Text: In swimming pool Zone 0, no switchgear or controlgear, including socket-outlets, shall be installed.

Visual Target: No switches/sockets in pool Zone 0

[SL-007]  SBC Ref: 702:52-2.8.104    Detection: ABSENCE    Priority: HIGH

Rule Text: Junction boxes shall not be installed in swimming pool Zone 0. In Zone 1, only SELV junction boxes are permitted and shall have IPX5 minimum and openable only by key or tool.

Visual Target: No junction boxes in pool Zone 0; only IPX5 SELV boxes in Zone 1

[SL-008]  SBC Ref: 702:51-2.2    Detection: LABEL    Priority: HIGH

Rule Text: Electrical equipment in swimming pool zones shall have at least the IP code according to Table 702-1 (IPX8 for Zone 0, IPX5 for Zone 1, IPX4 for Zone 2).

Visual Target: IP rating mark on equipment in pool zones

[SL-009]  SBC Ref: 710:41    Detection: PRESENCE    Priority: HIGH

Rule Text: Medical locations: RCDs with rated residual operating current not exceeding 30 mA shall be provided for socket-outlets in medical locations of Group 1 and Group 2.

Visual Target: RCD (30 mA) for medical location socket-outlets

[SL-010]  SBC Ref: 710:53-7    Detection: PRESENCE    Priority: HIGH

Rule Text: Medical IT system monitoring: insulation monitoring devices shall be provided for medical IT systems with visual and audible alarms.

Visual Target: Insulation monitoring device with alarm in medical IT system

[SL-011]  SBC Ref: 710:51-4    Detection: LABEL    Priority: HIGH

Rule Text: Medical location circuits and equipment shall be identified to indicate their group classification (Group 0, 1, or 2) and safety service classification.

Visual Target: Group classification label on medical location distribution boards

[SL-012]  SBC Ref: 722:55-101    Detection: PRESENCE    Priority: HIGH

Rule Text: EV charging: socket-outlets and vehicle connectors for electric vehicle charging shall be of a type specifically identified for EV charging purposes.

Visual Target: EV-rated socket-outlet/connector at charging point

[SL-013]  SBC Ref: 722:53-6    Detection: PRESENCE    Priority: HIGH

Rule Text: EV charging circuits shall be provided with a means of isolation accessible to the user.

Visual Target: Isolation device at EV charging station

[SL-014]  SBC Ref: 720:3-101    Detection: LABEL    Priority: HIGH

Rule Text: Hazardous locations: zones shall be classified (Zone 0, 1, 2 for gas; Zone 20, 21, 22 for dust) and equipment shall bear marking appropriate to the zone classification.

Visual Target: Zone-classified equipment marking in hazardous areas

[SL-015]  SBC Ref: 720:52    Detection: CONDITION    Priority: HIGH

Rule Text: Wiring systems in hazardous locations shall be of a type specified for the zone. Cable entries into enclosures shall maintain the type of protection (e.g., flameproof, increased safety).

Visual Target: Correct cable entry/enclosure type in hazardous zones

# 8. Earthing & Bonding Visual Rules

The following 10 rules are extracted from Ch. 54 of SBC 401-CR-2024. Each rule block contains the SBC reference code, the full rule text, the detection type, the visual detection target, and the priority level.

[EB-001]  SBC Ref: 54-2.1.2    Detection: PRESENCE    Priority: HIGH

Rule Text: Where provided, earth electrodes within an installation shall be connected to the main earthing terminal using an earthing conductor.

Visual Target: Earthing conductor from electrode to MET

[EB-002]  SBC Ref: 54-2.4    Detection: PRESENCE    Priority: HIGH

Rule Text: A main earthing terminal (MET) shall be provided in every installation and shall be accessible for connection and testing.

Visual Target: Main earthing terminal present and accessible

[EB-003]  SBC Ref: 54-3.2    Detection: COLOR    Priority: HIGH

Rule Text: Protective conductors shall have green-and-yellow color identification throughout their length. PEN conductors shall be identified by blue marking at terminations in addition to green-yellow.

Visual Target: Green-yellow PE conductor; blue-marked PEN conductor

[EB-004]  SBC Ref: 54-3.8    Detection: POSITION    Priority: MEDIUM

Rule Text: Protective conductors shall be routed so as to minimize the possibility of damage or inadvertent disconnection during normal use or maintenance.

Visual Target: PE conductor routing and physical protection

[EB-005]  SBC Ref: 54-4.1    Detection: PRESENCE    Priority: HIGH

Rule Text: Protective bonding conductors for connection to the main earthing terminal shall connect all extraneous-conductive-parts including water pipes, gas pipes, heating systems, and air-conditioning.

Visual Target: Bonding conductors on water/gas/heating/AC pipes

[EB-006]  SBC Ref: 54-4.2    Detection: PRESENCE    Priority: HIGH

Rule Text: Protective bonding conductors for supplementary bonding shall be provided where required by the protective measures (e.g., bathrooms, medical locations).

Visual Target: Supplementary bonding conductors in special locations

[EB-007]  SBC Ref: 54-2.2    Detection: CONDITION    Priority: MEDIUM

Rule Text: Earth electrodes shall be of a type and installed in a manner that provides a reliable connection to earth. Concrete-embedded foundation earth electrodes shall be at least 5 cm deep in concrete.

Visual Target: Foundation earth electrode properly embedded in concrete

[EB-008]  SBC Ref: B.54-1    Detection: PRESENCE    Priority: HIGH

Rule Text: The main earthing terminal shall be connected to: foundation earth electrode or soil-embedded earth electrode, earth electrode for lightning protection system (if any), and metallic water/gas/heating service pipes entering the building.

Visual Target: MET connections to electrodes and services

[EB-009]  SBC Ref: 54-2.3    Detection: LABEL    Priority: MEDIUM

Rule Text: Earthing conductors shall be identified and accessible for inspection and testing. Connection points shall be accessible.

Visual Target: Earthing conductor identification and accessible connections

[EB-010]  SBC Ref: 54-5    Detection: PRESENCE    Priority: LOW

Rule Text: Functional earthing and functional-equipotential-bonding for ICT equipment shall be provided where required, with a main functional earthing terminal (MFET) if needed.

Visual Target: Functional earthing terminal for ICT equipment

# 9. Emergency & Safety Service Rules

The following 8 rules are extracted from Ch. 56, 710, 718 of SBC 401-CR-2024. Each rule block contains the SBC reference code, the full rule text, the detection type, the visual detection target, and the priority level.

[ES-001]  SBC Ref: 56-0.9    Detection: PRESENCE    Priority: HIGH

Rule Text: Emergency lighting applications: emergency lighting shall be provided in locations where loss of normal lighting could cause danger. Emergency luminaires shall be clearly identifiable.

Visual Target: Emergency luminaire presence and identification

[ES-002]  SBC Ref: 56-0.10    Detection: PRESENCE    Priority: HIGH

Rule Text: Fire protection applications or equipment: electrical supplies for fire pumps, fire detection and alarm systems, smoke control systems shall be independently supplied and clearly identified.

Visual Target: Fire protection equipment supply identification

[ES-003]  SBC Ref: 56-0.8    Detection: CONDITION    Priority: HIGH

Rule Text: Wiring systems for safety services shall be selected and erected to maintain functionality for the required duration under fire conditions. Fire-resistant cables shall be used where specified.

Visual Target: Fire-rated cable for safety service circuits

[ES-004]  SBC Ref: C.56    Detection: PRESENCE    Priority: HIGH

Rule Text: Fire switch: where a fire switch is required, it shall be red, clearly labeled, and installed at a readily accessible location near the main entrance to the building or area served.

Visual Target: Red fire switch near main entrance with label

[ES-005]  SBC Ref: 56-0.6    Detection: PRESENCE    Priority: HIGH

Rule Text: Electrical sources for safety services shall be independent of the normal supply and clearly identified. Standby generators or battery systems shall be installed in dedicated locations.

Visual Target: Identified safety service power source (generator/battery)

[ES-006]  SBC Ref: 56-0.7    Detection: LABEL    Priority: HIGH

Rule Text: Electrical circuits of safety services shall be independently identified and segregated from other circuits throughout the installation.

Visual Target: Safety service circuit identification and segregation

[ES-007]  SBC Ref: 718:83    Detection: PRESENCE    Priority: HIGH

Rule Text: Fire detection and alarm systems in communal facilities and workplaces shall be provided and shall be clearly identifiable.

Visual Target: Fire alarm devices (detectors, call points, sounders) visible in communal areas

[ES-008]  SBC Ref: 710:56    Detection: PRESENCE    Priority: HIGH

Rule Text: Medical locations: safety service electrical supplies for medical locations shall be provided per group classification. Group 2 locations require uninterruptible power supply for safety lighting and medical IT systems.

Visual Target: UPS/safety supply equipment in medical Group 2 locations

# 10. IP Rating & Environmental Marking Rules

The following 8 rules are extracted from Ch. 51, 55, 702, 704, 705, 710, 720 of SBC 401-CR-2024. Each rule block contains the SBC reference code, the full rule text, the detection type, the visual detection target, and the priority level.

[IP-001]  SBC Ref: 51-2.2    Detection: LABEL    Priority: HIGH

Rule Text: Electrical equipment shall be selected and erected in accordance with the requirements of Table 51-1 indicating the characteristics of equipment according to the external influences. IP code marking shall be visible on enclosures.

Visual Target: IP code mark on electrical enclosures

[IP-002]  SBC Ref: 55-9.10.1    Detection: LABEL    Priority: HIGH

Rule Text: Luminaires installed in wet locations shall have at least IPX4 unless otherwise specified. IP marking shall be visible on the luminaire.

Visual Target: IPX4+ marking on luminaires in wet locations

[IP-003]  SBC Ref: 702:51-2.2    Detection: LABEL    Priority: HIGH

Rule Text: Swimming pool and fountain equipment shall have at least the IP code according to Table 702-1 (Zone 0: IPX8; Zone 1: IPX5; Zone 2: IPX4).

Visual Target: IP rating mark on pool/fountain zone equipment

[IP-004]  SBC Ref: 704:51-2    Detection: LABEL    Priority: MEDIUM

Rule Text: Construction and demolition site installations: equipment shall have a degree of protection of at least IP44.

Visual Target: IP44+ marking on construction site equipment

[IP-005]  SBC Ref: 705:51-2    Detection: LABEL    Priority: MEDIUM

Rule Text: Agricultural and horticultural premises: equipment shall have a degree of protection of at least IP44 for indoor locations and IP54 for outdoor locations.

Visual Target: IP44/IP54 marking on agricultural premises equipment

[IP-006]  SBC Ref: 710:51-2    Detection: LABEL    Priority: HIGH

Rule Text: Medical locations: equipment shall have at least IPX1 for Group 0 locations and IPX4 for areas where cleaning with water jets is used.

Visual Target: IP rating marking on medical location equipment

[IP-007]  SBC Ref: 720:51    Detection: LABEL    Priority: HIGH

Rule Text: Hazardous locations: equipment shall bear the appropriate Ex marking and IP protection rating for the zone classification in which it is installed.

Visual Target: Ex marking and IP rating on hazardous zone equipment

[IP-008]  SBC Ref: 51-2.2.2    Detection: CONDITION    Priority: MEDIUM

Rule Text: If equipment does not have the characteristics relevant to the external influences of its location, it may be used provided it is provided with appropriate additional protection (e.g., additional enclosure). The additional enclosure shall be visually identifiable.

Visual Target: Additional protective enclosure around under-rated equipment

# 11. Verification Inspection Visual Rules

The following 12 rules are extracted from Ch. 61 of SBC 401-CR-2024. Each rule block contains the SBC reference code, the full rule text, the detection type, the visual detection target, and the priority level.

[VI-001]  SBC Ref: 61-4.2.2a    Detection: PRESENCE    Priority: HIGH

Rule Text: Initial verification inspection shall confirm: method of protection against electric shock is correctly implemented (barriers, enclosures, insulation visible).

Visual Target: Protective measures against electric shock visibly implemented

[VI-002]  SBC Ref: 61-4.2.2b    Detection: PRESENCE    Priority: HIGH

Rule Text: Initial verification inspection shall confirm: presence of fire barriers and other precautions against propagation of fire and protection against thermal effects.

Visual Target: Fire barriers at cable penetrations present and intact

[VI-003]  SBC Ref: 61-4.2.2f    Detection: PRESENCE    Priority: HIGH

Rule Text: Initial verification inspection shall confirm: selection, location and installation of suitable isolating and switching devices.

Visual Target: Isolation and switching devices present and correctly located

[VI-004]  SBC Ref: 61-4.2.2g    Detection: LABEL    Priority: MEDIUM

Rule Text: Initial verification inspection shall confirm: selection of equipment and protective measures appropriate to external influences and mechanical stresses.

Visual Target: Equipment type marking matching environmental conditions

[VI-005]  SBC Ref: 61-4.2.2h    Detection: COLOR    Priority: HIGH

Rule Text: Initial verification inspection shall confirm: identification of neutral and protective conductors by color and/or marking.

Visual Target: Correct conductor colors (PE: green-yellow, N: blue)

[VI-006]  SBC Ref: 61-4.2.2i    Detection: PRESENCE    Priority: MEDIUM

Rule Text: Initial verification inspection shall confirm: presence of diagrams, warning notices or similar information.

Visual Target: Diagrams and warning notices present at distribution board

[VI-007]  SBC Ref: 61-4.2.2j    Detection: LABEL    Priority: HIGH

Rule Text: Initial verification inspection shall confirm: identification of circuits, overcurrent protective devices, switches, terminals, etc.

Visual Target: Circuit labels on protective devices, switches, terminals

[VI-008]  SBC Ref: 61-4.2.2k    Detection: CONDITION    Priority: HIGH

Rule Text: Initial verification inspection shall confirm: adequacy of termination and connection of cables and conductors (no loose wires, proper lug connections).

Visual Target: Proper cable terminations (no loose/missing lugs)

[VI-009]  SBC Ref: 61-4.2.2l    Detection: PRESENCE    Priority: HIGH

Rule Text: Initial verification inspection shall confirm: selection and installation of earthing arrangements, protective conductors and their connections.

Visual Target: Earthing arrangement and PE connections present and visible

[VI-010]  SBC Ref: 61-4.2.2m    Detection: CONDITION    Priority: MEDIUM

Rule Text: Initial verification inspection shall confirm: accessibility of equipment for convenience of operation, identification, and maintenance.

Visual Target: Equipment accessible; no obstructions blocking access

[VI-011]  SBC Ref: 61-4.2.2o    Detection: CONDITION    Priority: HIGH

Rule Text: Initial verification inspection shall confirm: exposed-conductive-parts are connected to the earthing arrangement.

Visual Target: Exposed-conductive-parts bonded to earthing system

[VI-012]  SBC Ref: 61-4.2.2p    Detection: CONDITION    Priority: MEDIUM

Rule Text: Initial verification inspection shall confirm: selection and erection of wiring systems (correct type, routing, support).

Visual Target: Wiring system type, routing, and supports correct

# 12. Physical Protection Rules

The following 10 rules are extracted from Ch. 41 of SBC 401-CR-2024. Each rule block contains the SBC reference code, the full rule text, the detection type, the visual detection target, and the priority level.

[PP-001]  SBC Ref: 41-2.2.1.1    Detection: LABEL    Priority: HIGH

Rule Text: Electrical equipment having double or reinforced insulation (Class II equipment) shall be type tested and marked to the relevant standards, identified by the symbol IEC 60417-5172.

Visual Target: Class II equipment symbol (double square) on electrical equipment

[PP-002]  SBC Ref: 41-2.2.1.2    Detection: LABEL    Priority: HIGH

Rule Text: Electrical equipment having basic insulation only with supplementary insulation applied during erection shall have the symbol IEC 60417 5019 fixed in a visible position on the exterior and interior of the enclosure.

Visual Target: Supplementary insulation symbol on enclosure exterior and interior

[PP-003]  SBC Ref: 41-2.2.1.3    Detection: LABEL    Priority: HIGH

Rule Text: Electrical equipment having uninsulated live parts with reinforced insulation applied during erection shall have the symbol IEC 60417 5019 fixed in a visible position on the exterior and interior of the enclosure.

Visual Target: Reinforced insulation symbol on enclosure exterior and interior

[PP-004]  SBC Ref: 41-2.2.2.1    Detection: CONDITION    Priority: MEDIUM

Rule Text: All conductive parts separated from live parts by basic insulation only shall be contained in an insulating enclosure affording at least IPXXB or IP2X degree of protection.

Visual Target: Insulating enclosure with IP2X/IPXXB protection around conductive parts

[PP-005]  SBC Ref: 41-2.2.2.3    Detection: CONDITION    Priority: HIGH

Rule Text: Where lids or doors in the insulating enclosure can be opened without a tool or key, all conductive parts accessible when open shall be behind an insulating barrier (IPXXB or IP2X), removable only by tool or key.

Visual Target: Insulating barrier behind opened door/lid preventing contact with conductive parts

[PP-006]  SBC Ref: 41-2.2.2.4    Detection: LABEL    Priority: MEDIUM

Rule Text: Conductive parts enclosed in the insulating enclosure shall not be connected to a protective conductor. PE terminals inside the enclosure shall be marked as PE terminals.

Visual Target: PE terminal marking inside Class II enclosure

[PP-007]  SBC Ref: 41-1.7.5    Detection: CONDITION    Priority: MEDIUM

Rule Text: Plugs and socket-outlets for FELV systems shall not be able to enter socket-outlets of other voltage systems, socket-outlets shall not admit plugs of other voltage systems, and socket-outlets shall have a protective conductor contact.

Visual Target: FELV-specific plug/socket that is incompatible with other voltage systems

[PP-008]  SBC Ref: 41-4.4.3    Detection: CONDITION    Priority: MEDIUM

Rule Text: Plugs and socket-outlets in SELV and PELV systems shall not be able to enter socket-outlets of other voltage systems and shall not have a protective conductor contact (for SELV).

Visual Target: SELV/PELV-specific plug/socket incompatible with other voltage systems

[PP-009]  SBC Ref: 41-3.3.4    Detection: CONDITION    Priority: MEDIUM

Rule Text: Flexible cables and cords in separated circuits shall be visible throughout any part of their length liable to mechanical damage.

Visual Target: Visible flexible cable/cord run without concealed sections in damage-prone areas

[PP-010]  SBC Ref: 41-1.6.3.1    Detection: PRESENCE    Priority: HIGH

Rule Text: Where an IT system is designed not to disconnect on first fault, the occurrence of the first fault shall be indicated by either an insulation monitoring device (IMD) or a residual current monitor (RCM), with audible and/or visual signal.

Visual Target: Insulation monitoring device (IMD) with alarm indicator in IT system

# 13. Thermal Protection Rules

The following 13 rules are extracted from Ch. 42 of SBC 401-CR-2024. Each rule block contains the SBC reference code, the full rule text, the detection type, the visual detection target, and the priority level.

[TH-001]  SBC Ref: 42-1.2    Detection: SPACING    Priority: HIGH

Rule Text: Fixed equipment which may attain surface temperatures causing a fire hazard shall be mounted on/within or screened by materials that will withstand such temperatures, or mounted at a sufficient distance from any material on which temperatures could have deleterious thermal effects.

Visual Target: Heat-producing equipment with clearance to combustible materials or heat shielding

[TH-002]  SBC Ref: 42-1.3    Detection: CONDITION    Priority: HIGH

Rule Text: Where arcs or sparks may be emitted by permanently connected equipment, the equipment shall be totally enclosed in arc-resistant material, or screened by arc-resistant material, or mounted at sufficient distance for safe extinction of emissions.

Visual Target: Arc-resistant enclosure or screening around arc-producing equipment

[TH-003]  SBC Ref: 42-1.5    Detection: PRESENCE    Priority: MEDIUM

Rule Text: Where electrical equipment contains flammable liquid in significant quantity (>25L), adequate precautions shall be taken to prevent the spread of liquid, flame and products of combustion (e.g. retention pit, sills, fire-resistant chamber).

Visual Target: Retention pit or sill or fire-resistant chamber around equipment with flammable liquid

[TH-004]  SBC Ref: 42-1.6    Detection: CONDITION    Priority: MEDIUM

Rule Text: Enclosures installed around electrical equipment shall withstand the highest temperature likely to be produced. Combustible materials are not suitable unless covered with non-combustible or not readily combustible material of low thermal conductivity.

Visual Target: Non-combustible enclosure material around electrical equipment

[TH-005]  SBC Ref: 42-2.2.2    Detection: CONDITION    Priority: MEDIUM

Rule Text: In conditions BD2, BD3, BD4 (difficult evacuation), switchgear and controlgear in passages shall be enclosed in cabinets of non-combustible or not readily combustible material.

Visual Target: Non-combustible switchgear cabinet in escape route/passage

[TH-006]  SBC Ref: 42-2.2.3    Detection: ABSENCE    Priority: MEDIUM

Rule Text: In conditions BD3, BD4 and in escape routes, electrical equipment containing flammable liquids shall not be installed.

Visual Target: Absence of equipment containing flammable liquids in escape routes

[TH-007]  SBC Ref: 42-2.3.1    Detection: SPACING    Priority: HIGH

Rule Text: Luminaires shall be kept at adequate distance from combustible materials. Spotlights and projectors: 100W or less min 0.5m, >100-300W min 0.8m, >300-500W min 1.0m. A luminaire with a lamp that could eject flammable materials shall have a safety protective shield.

Visual Target: Luminaire clearance to combustible materials with protective shield for ejecting lamps

[TH-008]  SBC Ref: 42-2.3.3    Detection: CONDITION    Priority: HIGH

Rule Text: Switchgear for protection, control and isolation in BE2 (fire risk) locations shall be placed outside unless in an enclosure providing at least IP4X, or IP5X in presence of dust, or IP6X for conductive dust.

Visual Target: IP4X/IP5X/IP6X enclosure for switchgear in fire risk location

[TH-009]  SBC Ref: 42-2.3.12    Detection: ABSENCE    Priority: MEDIUM

Rule Text: PEN conductors are not allowed in locations where condition BE2 (fire risk) applies, except for circuits traversing such locations with no connection between the PEN conductor and any conductive part.

Visual Target: Absence of PEN conductor connections in fire risk (BE2) locations

[TH-010]  SBC Ref: 42-2.3.13    Detection: PRESENCE    Priority: HIGH

Rule Text: Every circuit supplying equipment in BE2 locations shall be provided with a means of isolation from all live supply conductors such that no live supply conductor can remain closed when others are open (mechanically linked switch).

Visual Target: Mechanically linked isolation device for circuits in fire risk locations

[TH-011]  SBC Ref: 42-2.4.1    Detection: CONDITION    Priority: LOW

Rule Text: Boxes and enclosures installed in prefabricated hollow walls liable to be drilled shall have a degree of protection of at least IP3X.

Visual Target: IP3X box/enclosure in hollow wall

[TH-012]  SBC Ref: 42-4.1    Detection: CONDITION    Priority: MEDIUM

Rule Text: Supporting parts, frames and enclosures of heating elements in forced air heating systems shall be of non-combustible material.

Visual Target: Non-combustible frame/enclosure of forced air heating element

[TH-013]  SBC Ref: 42-4.3    Detection: CONDITION    Priority: MEDIUM

Rule Text: Frame and enclosure of space heating appliances shall be of non-combustible material. Radiant heaters should be mounted with safety distance of at least 2m from flammable parts.

Visual Target: Non-combustible enclosure of space heater and 2m clearance from flammable materials

# 14. EMI & Special Installation Rules

This section covers vision-detectable rules from Chapter 44 (Electromagnetic Interference) and from special installation sections 712 through 717, including photovoltaic systems, sauna rooms, construction sites, agricultural premises, confined locations, caravan parks, marinas, exhibitions, outdoor lighting, extra-low voltage lighting, and mobile/transportable units. These rules address specialized environments with unique visual compliance requirements.

## EM — EMI Protection Rules

Source: Ch. 44 of SBC 401-CR-2024. 5 rules.

[EM-001]  SBC Ref: 44-4.4.2b    Detection: CONDITION    Priority: MEDIUM

Rule Text: Metal sheaths of cables should be bonded to the Common Bonding Network (CBN).

Visual Target: Bonded metal cable sheath connection to CBN

[EM-002]  SBC Ref: 44-4.4.2h    Detection: SPACING    Priority: MEDIUM

Rule Text: Where a lightning protection system is installed, power and signal cables shall be separated from the down conductors of the LPS by either a minimum distance or by use of screening.

Visual Target: Separation between power/signal cables and lightning protection down conductors

[EM-003]  SBC Ref: 44-4.4.8    Detection: CONDITION    Priority: HIGH

Rule Text: Metal pipes and metal armouring of cables entering a building shall be bonded to the main earthing terminal by means of conductors having low impedance.

Visual Target: Bonding connection from metal pipe/cable armour to main earthing terminal at building entry

[EM-004]  SBC Ref: 44-4.5.5    Detection: COLOR    Priority: MEDIUM

Rule Text: Functional earthing conductors shall not use the green-and-yellow color reserved for earthing conductors. It is recommended to use the same color throughout the whole installation to mark functional earthing conductors at each end.

Visual Target: Functional earthing conductor color (not green-yellow, preferably pink)

[EM-005]  SBC Ref: 44-4.6.2    Detection: SPACING    Priority: MEDIUM

Rule Text: Where the specification of ICT cable is not available, the cable separation distance between power and ICT cables shall be not less than 200mm in free air.

Visual Target: Minimum 200mm separation between power cables and ICT cables

## PV — Photovoltaic Installation Rules

Source: Sec. 712 of SBC 401-CR-2024. 12 rules.

[PV-001]  SBC Ref: 712:41-2.101    Detection: CONDITION    Priority: HIGH

Rule Text: Equipment on the DC side of PV installations (PV modules, distribution boards, cabinets) shall be Class II or equivalent insulation according to IEC 61140.

Visual Target: Class II or equivalent insulation marking on PV DC-side equipment

[PV-002]  SBC Ref: 712:51-0.3    Detection: CONDITION    Priority: HIGH

Rule Text: Equipment in outdoor PV locations shall have a degree of protection of at least IP44 and a degree of protection against external mechanical impact not less than IK07.

Visual Target: IP44 and IK07 rated equipment in outdoor PV installation

[PV-003]  SBC Ref: 712:51-4.101    Detection: LABEL    Priority: HIGH

Rule Text: A sign indicating the presence of a photovoltaic installation shall be fixed at the origin of the electrical installation, at the metering position (if remote), and at the consumer unit/distribution board to which the PCE supply is connected.

Visual Target: PV installation warning sign at origin, meter position, and distribution board

[PV-004]  SBC Ref: 712:51-4.102    Detection: LABEL    Priority: HIGH

Rule Text: Each point of access to live parts on the DC side (distribution boards, cabinets) shall have a permanent marking bearing the text 'SOLAR DC - Live parts can remain energized after isolation'.

Visual Target: Permanent 'SOLAR DC - Live parts can remain energized' marking on DC-side access points

[PV-005]  SBC Ref: 712:51-4.106.1    Detection: LABEL    Priority: HIGH

Rule Text: Disconnection devices shall be marked with an identification name or number according to the PV array wiring diagram. All switches shall have the ON and OFF positions clearly indicated.

Visual Target: Identification label and ON/OFF position indicator on PV disconnection devices

[PV-006]  SBC Ref: 712:51-4.106.2    Detection: LABEL    Priority: HIGH

Rule Text: The PV array DC switch disconnector shall be identified by a sign affixed in a prominent location adjacent to the switch disconnector. Where multiple disconnection devices are not ganged, signage shall warn of multiple DC sources.

Visual Target: Identification sign adjacent to PV array DC switch disconnector

[PV-007]  SBC Ref: 712:51-4.2    Detection: COLOR    Priority: HIGH

Rule Text: The identification of AC and DC circuits shall be such that they are clearly distinguishable from each other (e.g. by labels or different colored cables).

Visual Target: Distinguishable AC and DC circuit cables (different colors or labels)

[PV-008]  SBC Ref: 712:4.102    Detection: COLOR    Priority: MEDIUM

Rule Text: A cable used for functional earthing in PV installations shall not be identified by the color combination green and yellow. It is recommended to use the color pink.

Visual Target: Functional earthing conductor in PV (pink color, not green-yellow)

[PV-009]  SBC Ref: 712:52-6    Detection: ABSENCE    Priority: HIGH

Rule Text: Plugs and socket-outlets normally used for the connection of household equipment to low voltage AC power shall not be used in PV arrays.

Visual Target: Absence of standard household AC plugs/sockets in PV array

[PV-010]  SBC Ref: 712:52-6.101    Detection: CONDITION    Priority: HIGH

Rule Text: Connectors on the DC side of PV installations shall be especially suitable for the DC side. Connectors accessible to non-skilled persons shall be disconnectable only by key or tool, or installed within a lockable enclosure.

Visual Target: PV DC-specific connector with key/tool lock or in lockable enclosure

[PV-011]  SBC Ref: 712:52-6.102    Detection: CONDITION    Priority: MEDIUM

Rule Text: Where conductors enter a PV combiner box without conduit, a tension relief arrangement (e.g. gland connector) shall be used. All cable entries shall maintain the IP rating of the enclosure.

Visual Target: Tension relief/gland connector at PV combiner box cable entries maintaining IP rating

[PV-012]  SBC Ref: 712:51-4.103    Detection: LABEL    Priority: MEDIUM

Rule Text: All PCEs should bear a marking indicating that, before any servicing operation, the PCE shall be isolated from all supplies.

Visual Target: Isolation warning marking on PCE (power conditioning equipment)

## SN — Sauna Location Rules

Source: Sec. 703 of SBC 401-CR-2024. 4 rules.

[SN-001]  SBC Ref: 703:51-2.2    Detection: CONDITION    Priority: HIGH

Rule Text: Equipment in sauna rooms shall have at least IP24 degree of protection. If cleaning by water jets may be expected, equipment shall be at least IPX5.

Visual Target: IP24 (or IPX5) rated equipment in sauna room

[SN-002]  SBC Ref: 703:53-6.5    Detection: ABSENCE    Priority: HIGH

Rule Text: Socket-outlets shall not be erected within the location containing the sauna heater.

Visual Target: Absence of socket-outlets inside sauna room

[SN-003]  SBC Ref: 703:53-6.5    Detection: POSITION    Priority: HIGH

Rule Text: Switchgear and controlgear for lighting (not part of sauna heater) shall be placed outside the sauna room or cabin.

Visual Target: Switchgear and controlgear for sauna lighting mounted outside sauna room

[SN-004]  SBC Ref: 703:52-2    Detection: CONDITION    Priority: MEDIUM

Rule Text: Metallic sheaths and metallic conduits in sauna rooms shall not be accessible in normal use.

Visual Target: Inaccessible metallic sheaths/conduits in sauna room

## CS — Construction Site Rules

Source: Sec. 704 of SBC 401-CR-2024. 2 rules.

[CS-001]  SBC Ref: 704:53-6.2.2    Detection: CONDITION    Priority: HIGH

Rule Text: Each assembly for construction sites (ACS) shall incorporate devices for isolating the incoming supply, suitable for securing in the off position (e.g. padlocking facility or lockable enclosure).

Visual Target: Lockable isolation device (padlock facility) on construction site assembly

[CS-002]  SBC Ref: 704:52-2.8.101    Detection: CONDITION    Priority: MEDIUM

Rule Text: Cables should not be run across site roads or walkways. Where necessary, special protection against mechanical damage shall be provided.

Visual Target: Mechanical protection for cables crossing construction site roads/walkways

## AG — Agricultural Premises Rules

Source: Sec. 705 of SBC 401-CR-2024. 7 rules.

[AG-001]  SBC Ref: 705:51-2.2    Detection: CONDITION    Priority: HIGH

Rule Text: In agricultural or horticultural premises, electrical equipment shall have a minimum degree of protection of IP44. Where IP44 is not available, equipment shall be placed in an IP44-complying enclosure.

Visual Target: IP44 rated electrical equipment or enclosure in agricultural premises

[AG-002]  SBC Ref: 705:51-3.2    Detection: POSITION    Priority: HIGH

Rule Text: Electrical equipment generally shall be inaccessible to livestock. Equipment unavoidably accessible shall be adequately constructed and installed to avoid damage by and minimize risk of injury to livestock.

Visual Target: Electrical equipment positioned inaccessible to livestock or livestock-proof

[AG-003]  SBC Ref: 705:42-2.6    Detection: SPACING    Priority: MEDIUM

Rule Text: Radiant heaters in agricultural premises shall be installed at a distance of at least 0.5m from livestock and from combustible material unless a greater distance is specified by the manufacturer.

Visual Target: Radiant heater minimum 0.5m from livestock and combustible material in agricultural premises

[AG-004]  SBC Ref: 705:53    Detection: LABEL    Priority: MEDIUM

Rule Text: Only electrical heating appliances with visual indication of the operating position shall be used in agricultural premises.

Visual Target: Visual ON/OFF position indicator on electrical heating appliances in agricultural premises

[AG-005]  SBC Ref: 705:53-6.2    Detection: LABEL    Priority: MEDIUM

Rule Text: Isolation devices in agricultural premises shall be marked according to the part of the installation to which they belong. Devices for isolation and emergency stopping shall not be accessible to livestock.

Visual Target: Labeled isolation device in agricultural premises inaccessible to livestock

[AG-006]  SBC Ref: 705:51-4.4.3    Detection: LABEL    Priority: MEDIUM

Rule Text: A plan indicating the location of all electrical equipment, the routing of all concealed cables, a single line distribution diagram, and an equipotential bonding diagram shall be provided to the user of the installation.

Visual Target: Installation documentation/diagrams provided to user in agricultural premises

[AG-007]  SBC Ref: 705:55-9    Detection: LABEL    Priority: MEDIUM

Rule Text: In areas with fire risk and combustible dust coating, only luminaires marked in accordance with IEC 60598-2-24 (limited surface temperature) shall be used. Luminaires marked with 'not suitable for normally flammable surfaces' shall have IP54.

Visual Target: IEC 60598-2-24 marked luminaire (limited surface temperature) in agricultural fire risk area

## CR — Confined/Restricted Location Rules

Source: Sec. 706 of SBC 401-CR-2024. 2 rules.

[CR-001]  SBC Ref: 706:41-4.3.101    Detection: POSITION    Priority: MEDIUM

Rule Text: Sources for SELV and PELV in conducting locations with restricted movement shall be situated outside the conducting location, unless they are part of the fixed installation within the location.

Visual Target: SELV/PELV source positioned outside conducting location with restricted movement

[CR-002]  SBC Ref: 706:41-3.3.2    Detection: POSITION    Priority: MEDIUM

Rule Text: The source for electrical separation in conducting locations with restricted movement shall be situated outside the conducting location unless it is part of the fixed installation within the location.

Visual Target: Isolating transformer/source positioned outside conducting restricted location

## CV — Caravan/Camping Park Rules

Source: Sec. 708 of SBC 401-CR-2024. 5 rules.

[CV-001]  SBC Ref: 708:51-2.2.1.101    Detection: CONDITION    Priority: HIGH

Rule Text: Equipment in caravan/camping parks shall be selected with a degree of protection of at least IPX4 to protect against water splashes (AD4).

Visual Target: IPX4 rated equipment in caravan/camping park

[CV-002]  SBC Ref: 708:55.101.1    Detection: CONDITION    Priority: HIGH

Rule Text: Every socket-outlet in caravan parks shall comply with IEC 60309-2 and meet IP44 or such protection shall be provided by an enclosure. Socket-outlets shall be interlocked.

Visual Target: IEC 60309-2 compliant interlocked IP44 socket-outlet in caravan park

[CV-003]  SBC Ref: 708:55.101.3    Detection: CONDITION    Priority: MEDIUM

Rule Text: No more than four socket-outlets shall be grouped together in any one enclosure in caravan parks to maintain IP degree when in use.

Visual Target: Maximum 4 socket-outlets per enclosure in caravan park

[CV-004]  SBC Ref: 708:55.101.6    Detection: POSITION    Priority: HIGH

Rule Text: The lowest part of any socket-outlet in caravan/camping parks shall be placed at a height between 0.5m and 1.5m from the ground.

Visual Target: Socket-outlet height 0.5m-1.5m from ground in caravan/camping park

[CV-005]  SBC Ref: 708:52-1.7.103    Detection: CONDITION    Priority: HIGH

Rule Text: Every overhead conductor in caravan/camping parks shall be insulated. Overhead conductors shall be at a height above ground of not less than 6m in vehicle areas and 3.5m in other areas.

Visual Target: Insulated overhead conductor at minimum 6m/3.5m height in caravan park

## MR — Marina Rules

Source: Sec. 709 of SBC 401-CR-2024. 5 rules.

[MR-001]  SBC Ref: 709:51-2.2.1.1    Detection: CONDITION    Priority: HIGH

Rule Text: Equipment installed on or above a jetty/wharf/pier/pontoon in marinas shall be selected: IPX4 for water splashes, IPX5 for water jets, IPX6 for water waves.

Visual Target: IPX4/IPX5/IPX6 rated equipment on marina jetty/pontoon

[MR-002]  SBC Ref: 709:55-6.6.1    Detection: CONDITION    Priority: HIGH

Rule Text: Every socket-outlet in marinas (up to 63A) shall comply with IEC 60309-2 and meet IP44, or IPX5/IPX6 where AD5/AD6 applies.

Visual Target: IEC 60309-2 compliant IP44 socket-outlet in marina

[MR-003]  SBC Ref: 709:55-6.6.6    Detection: POSITION    Priority: HIGH

Rule Text: Every socket-outlet on fixed jetties/piers and floating pontoons in marinas shall be placed to avoid the effect of splashing and/or submersion.

Visual Target: Socket-outlet positioned to avoid splashing/submersion on marina jetty/pontoon

[MR-004]  SBC Ref: 709:52-1.8.3    Detection: CONDITION    Priority: MEDIUM

Rule Text: All overhead conductors in marinas shall be insulated. Overhead conductors shall be at a height above ground of not less than 6m in vehicle areas and 3.5m in other areas.

Visual Target: Insulated overhead conductor at minimum 6m/3.5m height in marina

[MR-005]  SBC Ref: 709:55-6.6.3    Detection: CONDITION    Priority: MEDIUM

Rule Text: No more than four socket-outlets shall be grouped together in any one enclosure in marinas.

Visual Target: Maximum 4 socket-outlets per enclosure in marina

## EX — Exhibition/Show Rules

Source: Sec. 711 of SBC 401-CR-2024. 7 rules.

[EX-001]  SBC Ref: 711:51.101    Detection: CONDITION    Priority: HIGH

Rule Text: Control and protective switchgear in exhibitions shall be placed in closed cabinets which can only be opened by the use of a key or a tool, except for parts designed to be operated by ordinary persons.

Visual Target: Key/tool-locked cabinet for switchgear in exhibition/show

[EX-002]  SBC Ref: 711:42-2.4.101    Detection: SPACING    Priority: HIGH

Rule Text: Lighting equipment with high temperature surfaces (incandescent lamps, spotlights, projectors) shall be suitably guarded and arranged well away from combustible material to prevent contact.

Visual Target: High-temperature lighting guarded and spaced from combustible material in exhibition

[EX-003]  SBC Ref: 711:55-9.3.101    Detection: POSITION    Priority: HIGH

Rule Text: Luminaires mounted below 2.5m (arm's reach) from floor level in exhibitions shall be firmly fixed and sited or guarded to prevent risk of injury or ignition of materials.

Visual Target: Firmly fixed/guarded luminaire below 2.5m in exhibition

[EX-004]  SBC Ref: 711:55-9.3.103.4    Detection: LABEL    Priority: HIGH

Rule Text: A separate circuit shall supply high-voltage signs/lamps in exhibitions, controlled by an emergency switch that is easily visible, accessible and marked.

Visual Target: Marked, visible, accessible emergency switch for high-voltage signage in exhibition

[EX-005]  SBC Ref: 711:52.101    Detection: CONDITION    Priority: MEDIUM

Rule Text: Flexible cables in exhibitions shall not be laid in areas accessible to the public unless protected against mechanical damage.

Visual Target: Mechanical protection for flexible cables in public areas of exhibition

[EX-006]  SBC Ref: 711:52-6.101    Detection: CONDITION    Priority: MEDIUM

Rule Text: Joints in cables in exhibitions shall be made using connectors or in an enclosure with at least IP4X or IPXXD degree of protection.

Visual Target: IP4X/IPXXD enclosure for cable joints in exhibition

[EX-007]  SBC Ref: 711:53-6.2.1.1    Detection: LABEL    Priority: HIGH

Rule Text: Every separate temporary structure in exhibitions shall be provided with its own readily accessible and properly identifiable means of isolation.

Visual Target: Readily accessible, identifiable isolation device for each exhibition stand/structure

## OL — Outdoor Lighting Rules

Source: Sec. 714 of SBC 401-CR-2024. 4 rules.

[OL-001]  SBC Ref: 714:A.41    Detection: CONDITION    Priority: HIGH

Rule Text: Enclosures of luminaires and lighting installations in external lighting shall prevent access to live parts without the use of a tool or key. All doors shall be lockable with a key or tool regardless of height.

Visual Target: Tool/key-locked enclosure doors for outdoor luminaires

[OL-002]  SBC Ref: 714:A.41    Detection: CONDITION    Priority: HIGH

Rule Text: For outdoor luminaires at a height of less than 2.8m above ground, access to the light source shall only be possible after removing a barrier or enclosure requiring the use of a tool.

Visual Target: Tool-removable barrier for light source access on outdoor luminaire below 2.8m

[OL-003]  SBC Ref: 714:51-2.2.5    Detection: CONDITION    Priority: HIGH

Rule Text: Electrical equipment in external lighting installations shall have at least IP33. Equipment mounted externally on lighting columns: at least IP44. Lanterns: at least IP54.

Visual Target: IP33/IP44/IP54 rated equipment/lanterns in outdoor lighting installation

[OL-004]  SBC Ref: 714:53-6.2.1.1    Detection: PRESENCE    Priority: MEDIUM

Rule Text: Every circuit in external lighting installations shall be capable of being individually isolated from each of the live supply conductors.

Visual Target: Individual circuit isolation device for each outdoor lighting circuit

## EL — Extra-low Voltage Lighting Rules

Source: Sec. 715 of SBC 401-CR-2024. 5 rules.

[EL-001]  SBC Ref: 715:52-1.1    Detection: ABSENCE    Priority: HIGH

Rule Text: Metallic structural parts of buildings (e.g. pipe systems, parts of furniture) shall not be used as live conductors in ELV lighting installations.

Visual Target: Absence of building structural parts used as live conductors in ELV lighting

[EL-002]  SBC Ref: 715:52-1.106    Detection: CONDITION    Priority: MEDIUM

Rule Text: Bare conductors in ELV lighting (25V ac or less or 60V dc or less) shall not be placed directly on combustible material. At least one conductor and its terminals shall be insulated between transformer and protective device.

Visual Target: Bare ELV conductors not on combustible material; insulated conductor between transformer and protective device

[EL-003]  SBC Ref: 715:52-1.107    Detection: CONDITION    Priority: MEDIUM

Rule Text: Suspension devices for ELV luminaires shall carry 5x the mass of luminaires, but not less than 5kg. Insulation piercing connectors and counterweight termination wires hung over suspended conductors shall not be used.

Visual Target: Adequate suspension device for ELV luminaire (5x mass, min 5kg), no piercing connectors

[EL-004]  SBC Ref: 715:52-1.107    Detection: CONDITION    Priority: MEDIUM

Rule Text: Suspended systems with bare conductors in ELV lighting shall be fixed to walls or ceilings by insulated fixing means and shall be continuously accessible throughout the route.

Visual Target: Insulated fixings and continuous accessibility for suspended bare ELV conductors

[EL-005]  SBC Ref: 715:53-0.3.104    Detection: LABEL    Priority: MEDIUM

Rule Text: If the identification of a protective device for a circuit in ELV lighting is not immediately evident, a sign or diagram (label) close to the protective device shall identify the circuit and its purpose.

Visual Target: Identification label/diagram near protective device for ELV lighting circuit

## MO — Mobile/Transportable Unit Rules

Source: Sec. 717 of SBC 401-CR-2024. 6 rules.

[MO-001]  SBC Ref: 717:51-4.1    Detection: LABEL    Priority: HIGH

Rule Text: A permanent notice of durable material shall be fixed to the mobile/transportable unit in a prominent position, preferably adjacent to the supply inlet connector, stating the type of supply, voltage rating, number of phases, earthing arrangement, and maximum power.

Visual Target: Permanent rating notice adjacent to supply inlet connector on mobile unit

[MO-002]  SBC Ref: 717:51-4.1    Detection: LABEL    Priority: MEDIUM

Rule Text: For socket-outlets individually protected by electrical separation in mobile units, a durable indication shall be located adjacent to these socket-outlets stating that only one item of equipment shall be connected to each socket-outlet.

Visual Target: Warning label at electrically separated socket-outlets: 'one item of equipment only'

[MO-003]  SBC Ref: 717:55-6.5.1.1    Detection: CONDITION    Priority: HIGH

Rule Text: Plugs on mobile/transportable units shall have an enclosure of insulating material. Plugs and socket-outlets located outside shall afford IP44. Appliance inlets shall provide at least IP55.

Visual Target: Insulating plug enclosure, IP44 socket-outlets, IP55 appliance inlets on mobile unit

[MO-004]  SBC Ref: 717:52-1.11    Detection: CONDITION    Priority: HIGH

Rule Text: The flexible cable connecting a mobile unit to supply shall enter the unit by an insulating inlet minimizing insulation damage risk. The cable sheath shall be firmly gripped by the cable gland or anchored to prevent stress on the termination.

Visual Target: Insulating cable inlet and firmly gripped/anchored cable gland on mobile unit

[MO-005]  SBC Ref: 717:31-2.2.1    Detection: ABSENCE    Priority: MEDIUM

Rule Text: The use of the TN-C system is not permitted inside any mobile or transportable unit.

Visual Target: Absence of TN-C system inside mobile/transportable unit

[MO-006]  SBC Ref: 717:55-6.5.1.1    Detection: POSITION    Priority: MEDIUM

Rule Text: The plug part for connecting the mobile/transportable unit to the supply shall be situated on the unit.

Visual Target: Supply plug situated on the mobile/transportable unit itself

# 15. Excluded Rules — Physical Testing Required

The following SBC 401 rule categories are excluded from this extraction because they require physical measurement, instrumented testing, or engineering calculation that cannot be performed by visual inspection. These rules should not be included in a vision-based compliance inspection vector database, as their verification inherently requires test instruments and cannot be confirmed by visual observation alone.

Documenting these excluded categories serves two purposes: first, it provides clarity on the scope boundary of the vision-detectable rule set; second, it prevents accidental inclusion of non-visual rules in the vector database, which would lead to false compliance claims if retrieved during visual inspection workflows.

| SBC 401 Reference | Rule Description | Testing Instrument Required |
| --- | --- | --- |
| 61-4.3.2 | Continuity of conductors: protective conductors, bonding conductors, ring final circuit live conductors | Low-resistance ohmmeter |
| 61-4.3.3 | Insulation resistance between live conductors and between live conductors and earth | Insulation resistance tester (megger) |
| 61-4.3.4 | Protection by SELV, PELV, double insulation, and electrical separation | Insulation resistance tester / voltage tester |
| 61-4.3.5 | Protection by barriers and enclosures during erection | Standard test finger / IP test probe |
| 61-4.3.6 | Protection by automatic disconnection: earth fault loop impedance | Earth fault loop impedance tester |
| 61-4.3.7 | Protection by automatic disconnection: RCD operation and trip time | RCD tester |
| 61-4.3.8 | Earth electrode resistance measurement | Earth resistance tester |
| 61-4.3.9 | Polarity verification | Voltage tester / polarity tester |
| 61-4.3.10 | Voltage drop verification | Voltage measurement at supply and load |
| 54-2.2 | Earth electrode resistance value | Earth resistance tester |
| 53-1.6 | RCD trip current and trip time measurement | RCD tester |
| 41-1.6.3 | IT system first fault current and impedance verification | Insulation monitoring / impedance tester |